## Main Hall-Sep-1
|  |  | CONTROL CHART FORM |  |  | Doc. No. | QCL-FRM-3.03
[6 empty] | Issue Date | 2023-09-05
[6 empty] | Issue# | 1
Measurand: |  |  | Room Temperature |  | Duration: | January-2024 (2nd Half)
Location: |  |  | Main Hall |  | Measuring device: | Wet & Dry Bulb Thermometer
Target Value (oC): |  |  | 25 |  | Device ID: | ESP-LAB-WDT-001
Lower Control Limit (oC): |  |  | 23 |  | Upper Control Limit: | 27 (oC)
Lower Action Limit (oC): |  |  | 21 |  | Upper Action Limit: | 29 (oC)
Value No. | Date | Day | Time | Measured Value (oC) | Deviation (oC) | Remarks | Action Taken, if any | No. | Target Value (oC) | Measured Value (oC) | Lower Control Limit | Upper Control Limit | Lower Action Limit | Upper Action Limit
1 | 2024-01-17 | Wednesday | 23:00 | 23.1 | -1.9 | Under Control | --- | 1 | 25 | 23.1 | 23 | 27 | 21 | 29
2 | 2024-01-17 | Wednesday | 3:00 | 23.7 | -1.3 | Under Control | --- | 2 | 25 | 23.7 | 23 | 27 | 21 | 29
3 | 2024-01-18 | Thursday | 23:00 | 23.2 | -1.8 | Under Control | --- | 3 | 25 | 23.2 | 23 | 27 | 21 | 29
4 | 2024-01-18 | Thursday | 3:00 | 22.6 | -2.4 | Under Control | --- | 4 | 25 | 22.6 | 23 | 27 | 21 | 29
5 | 2024-01-19 | Friday | 23:00 | 22.7 | -2.3 | Under Control | --- | 5 | 25 | 22.7 | 23 | 27 | 21 | 29
6 | 2024-01-19 | Friday | 3:00 | 23.5 | -1.5 | Under Control | --- | 6 | 25 | 23.5 | 23 | 27 | 21 | 29
7 | 2024-01-20 | Saturday | 23:00 | 22.9 | -2.1 | Under Control | --- | 7 | 25 | 22.9 | 23 | 27 | 21 | 29
8 | 2024-01-20 | Saturday | 3:00 | 22.5 | -2.5 | Under Control | --- | 8 | 25 | 22.5 | 23 | 27 | 21 | 29
9 | 2024-01-21 | Sunday | 23:00 | 23.1 | -1.9 | Under Control | --- | 9 | 25 | 23.1 | 23 | 27 | 21 | 29
10 | 2024-01-21 | Sunday | 3:00 | 23.5 | -1.5 | Under Control | --- | 10 | 25 | 23.5 | 23 | 27 | 21 | 29
11 | 2024-01-22 | Monday | 23:00 | 22.9 | -2.1 | Under Control | --- | 11 | 25 | 22.9 | 23 | 27 | 21 | 29
12 | 2024-01-22 | Monday | 3:00 | 22.5 | -2.5 | Under Control | --- | 12 | 25 | 22.5 | 23 | 27 | 21 | 29
13 | 2024-01-23 | Tuesday | 23:00 | 23.1 | -1.9 | Under Control | --- | 13 | 25 | 23.1 | 23 | 27 | 21 | 29
14 | 2024-01-23 | Tuesday | 3:00 | 23.5 | -1.5 | Under Control | --- | 14 | 25 | 23.5 | 23 | 27 | 21 | 29
15 | 2024-01-24 | Wednesday | 23:00 | 22.7 | -2.3 | Under Control | --- | 15 | 25 | 22.7 | 23 | 27 | 21 | 29
16 | 2024-01-24 | Wednesday | 3:00 | 23.5 | -1.5 | Under Control | --- | 16 | 25 | 23.5 | 23 | 27 | 21 | 29
17 | 2024-01-25 | Thursday | 23:00 | 23 | -2 | Under Control | --- | 17 | 25 | 23 | 23 | 27 | 21 | 29
18 | 2024-01-25 | Thursday | 3:00 | 22.8 | -2.2 | Under Control | --- | 18 | 25 | 22.8 | 23 | 27 | 21 | 29
19 | 2024-01-26 | Friday | 23:00 | 23.4 | -1.6 | Under Control | --- | 19 | 25 | 23.4 | 23 | 27 | 21 | 29
20 | 2024-01-26 | Friday | 3:00 | 22.9 | -2.1 | Under Control | --- | 20 | 25 | 22.9 | 23 | 27 | 21 | 29
21 | 2024-01-27 | Saturday | 23:00 | 23.1 | -1.9 | Under Control | --- | 21 | 25 | 23.1 | 23 | 27 | 21 | 29
22 | 2024-01-27 | Saturday | 3:00 | 23.7 | -1.3 | Under Control | --- | 22 | 25 | 23.7 | 23 | 27 | 21 | 29
23 | 2024-01-28 | Sunday | 23:00 | 23.2 | -1.8 | Under Control | --- | 23 | 25 | 23.2 | 23 | 27 | 21 | 29
24 | 2024-01-28 | Sunday | 3:00 | 22.6 | -2.4 | Under Control | --- | 24 | 25 | 22.6 | 23 | 27 | 21 | 29
25 | 2024-01-29 | Monday | 23:00 | 22.2 | -2.8 | Under Control | --- | 25 | 25 | 22.2 | 23 | 27 | 21 | 29
26 | 2024-01-29 | Monday | 3:00 | 23.1 | -1.9 | Under Control | --- | 26 | 25 | 23.1 | 23 | 27 | 21 | 29
27 | 2024-01-30 | Tuesday | 23:00 | 23.1 | -1.9 | Under Control | --- | 27 | 25 | 23.1 | 23 | 27 | 21 | 29
28 | 2024-01-30 | Tuesday | 3:00 | 22.7 | -2.3 | Under Control | --- | 28 | 25 | 22.7 | 23 | 27 | 21 | 29
29 | 2024-01-31 | Wednesday | 23:00 | 23.5 | -1.5 | Under Control | --- | 29 | 25 | 23.5 | 23 | 27 | 21 | 29
30 | 2024-01-31 | Wednesday | 3:00 | 22.8 | -2.2 | Under Control | --- | 30 | 25 | 22.8 | 23 | 27 | 21 | 29
[5 empty] | -25 |  | --- | 0 | 25 | 0 | 23 | 27 | 21 | 29
[5 empty] | -25 |  | --- | 0 | 25 | 0 | 23 | 27 | 21 | 29
Average | 23.0367 | Maximum Temp. | 23.7 | Minimum Temp. | 22.2 | Under Control | ---
Prepared By:
|  |  | Name |  |  | Signature | Date
Reviewed/Checked By:
|  |  | Name |  |  | Signature | Date