## Main Hall-Sep-1
|  |  | CONTROL CHART FORM |  |  | Doc. No. | QCL-FRM-3.03
[6 empty] | Issue Date | 2023-09-05
[6 empty] | Issue# | 1
Measurand: |  |  | Room Temperature |  | Duration: | September-2024 (2nd Half)
Location: |  |  | Main Hall |  | Measuring device: | Thermohygrometer
Target Value (oC): |  |  | 25 |  | Device ID: | ESP-LAB-WDT-001
Lower Control Limit (oC): |  |  | 23 |  | Upper Control Limit: | 27 (oC)
Lower Action Limit (oC): |  |  | 21 |  | Upper Action Limit: | 29 (oC)
Value No. | Date | Day | Time | Measured Value (oC) | Deviation (oC) | Remarks | Action Taken, if any | No. | Target Value (oC) | Measured Value (oC) | Lower Control Limit | Upper Control Limit | Lower Action Limit | Upper Action Limit
1 | 2024-09-16 | Monday | 23:00 | 25.3 | 0.3 | Under Control | --- | 1 | 25 | 25.3 | 23 | 27 | 21 | 29
2 | 2024-09-16 | Monday | 3:00 | 24.2 | -0.8 | Under Control | --- | 2 | 25 | 24.2 | 23 | 27 | 21 | 29
3 | 2024-09-18 | Wednesday | 23:00 | 25.1 | 0.1 | Under Control | --- | 3 | 25 | 25.1 | 23 | 27 | 21 | 29
4 | 2024-09-18 | Wednesday | 3:00 | 24.2 | -0.8 | Under Control | --- | 4 | 25 | 24.2 | 23 | 27 | 21 | 29
5 | 2024-09-19 | Thursday | 23:00 | 24.9 | -0.1 | Under Control | --- | 5 | 25 | 24.9 | 23 | 27 | 21 | 29
6 | 2024-09-19 | Thursday | 3:00 | 24.1 | -0.9 | Under Control | --- | 6 | 25 | 24.1 | 23 | 27 | 21 | 29
7 | 2024-09-20 | Friday | 23:00 | 24.2 | -0.8 | Under Control | --- | 7 | 25 | 24.2 | 23 | 27 | 21 | 29
8 | 2024-09-20 | Friday | 3:00 | 23.6 | -1.4 | Under Control | --- | 8 | 25 | 23.6 | 23 | 27 | 21 | 29
9 | 2024-09-21 | Saturday | 23:00 | 24.5 | -0.5 | Under Control | --- | 9 | 25 | 24.5 | 23 | 27 | 21 | 29
10 | 2024-09-21 | Saturday | 3:00 | 24.3 | -0.7 | Under Control | --- | 10 | 25 | 24.3 | 23 | 27 | 21 | 29
11 | 2024-09-22 | Sunday | 23:00 | 24.2 | -0.8 | Under Control | --- | 11 | 25 | 24.2 | 23 | 27 | 21 | 29
12 | 2024-09-22 | Sunday | 3:00 | 24 | -1 | Under Control | --- | 12 | 25 | 24 | 23 | 27 | 21 | 29
13 | 2024-09-23 | Monday | 23:00 | 24.1 | -0.9 | Under Control | --- | 13 | 25 | 24.1 | 23 | 27 | 21 | 29
14 | 2024-09-23 | Monday | 3:00 | 23.8 | -1.2 | Under Control | --- | 14 | 25 | 23.8 | 23 | 27 | 21 | 29
15 | 2024-09-24 | Tuesday | 23:00 | 24 | -1 | Under Control | --- | 15 | 25 | 24 | 23 | 27 | 21 | 29
16 | 2024-09-24 | Tuesday | 3:00 | 23.7 | -1.3 | Under Control | --- | 16 | 25 | 23.7 | 23 | 27 | 21 | 29
17 | 2024-09-25 | Wednesday | 23:00 | 24.4 | -0.6 | Under Control | --- | 17 | 25 | 24.4 | 23 | 27 | 21 | 29
18 | 2024-09-25 | Wednesday | 3:00 | 24 | -1 | Under Control | --- | 18 | 25 | 24 | 23 | 27 | 21 | 29
19 | 2024-09-26 | Thursday | 23:00 | 24 | -1 | Under Control | --- | 19 | 25 | 24 | 23 | 27 | 21 | 29
20 | 2024-09-26 | Thursday | 3:00 | 23.8 | -1.2 | Under Control | --- | 20 | 25 | 23.8 | 23 | 27 | 21 | 29
21 | 2024-09-27 | Friday | 23:00 | 24.1 | -0.9 | Under Control | --- | 21 | 25 | 24.1 | 23 | 27 | 21 | 29
22 | 2024-09-27 | Friday | 3:00 | 23.9 | -1.1 | Under Control | --- | 22 | 25 | 23.9 | 23 | 27 | 21 | 29
23 | 2024-09-28 | Saturday | 23:00 | 24 | -1 | Under Control | --- | 23 | 25 | 24 | 23 | 27 | 21 | 29
24 | 2024-09-28 | Saturday | 3:00 | 23.6 | -1.4 | Under Control | --- | 24 | 25 | 23.6 | 23 | 27 | 21 | 29
25 | 2024-09-29 | Sunday | 23:00 | 24.2 | -0.8 | Under Control | --- | 25 | 25 | 24.2 | 23 | 27 | 21 | 29
26 | 2024-09-29 | Sunday | 3:00 | 23.9 | -1.1 | Under Control | --- | 26 | 25 | 23.9 | 23 | 27 | 21 | 29
27 | 2024-09-30 | Monday | 23:00 | 24 | -1 | Under Control | --- | 27 | 25 | 24 | 23 | 27 | 21 | 29
28 | 2024-09-30 | Monday | 3:00 | 23.8 | -1.2 | Under Control | --- | 28 | 25 | 23.8 | 23 | 27 | 21 | 29
[8 empty] | 0 | 25 | 0 | 23 | 27 | 21 | 29
[8 empty] | 0 | 24.3 | 0 | 23 | 27 | 21 | 29
Average | 22.53 | Maximum | 25.3 | Minimum Temp. | 23.6 | Under Control | ---
Prepared By:
|  |  | Name |  |  | Signature | Date
Reviewed/Checked By:
|  |  | Name |  |  | Signature | Date